# Backwash Drum Filter S (RTF-S) page 1 / 2

STANDARD VERSION

Fully-automatic backwash filter with self-medium backwash without interruption of the filtration process during backwashing.

Backwash speed in the filter-element up to 10 m/s.

|  |  |
| --- | --- |
| **Operating conditions** |  |
| medium |  |  |
| flow rate | m³/h |  |
| working pressure | bar |  |
| filter fineness | µm |  |
| operating temperature | °C |  |
| flushing by | self-medium |
|  |  |
| **Design data** |  |
| main connection flanges acc. to DIN EN 1092 | DN |  |
| design pressure | 10 bar |
| test pressure | 14,3 bar |
| pressure loss with clean filter approx. | 0,1 bar |
| design temperature | 0 - 50 °C |
| construction and design | PED 2014/68/EU and AD 2000 |
|  |  |
| **Technical data** |  |
| weight empty approx. | kg |  |
| weight filled approx. | kg |  |
| volume | l |  |
|  |  |
| **Material** |  |
| filter housing | steel coated (RAL 3020) |
| filter element special slotted sieve | stainless steel 1.4435 (AISI 316 L) |
| drive shaft | stainless steel 1.4571 (AISI 316 Ti) |
| with wearing bushing | steel, chrome-oxyde coated |
|  |  |
| **Flushing water quantity** |  |
| duration of each backwash process | ~ 20 sec |
| flushing water quantity per each flushing process | l |  |

|  |  |
| --- | --- |
| Manufacturer | Dango & Dienenthal Filtertechnik GmbH |
|  | +49 271 401 41 23 |

# Automatic control for Backwash Drum Filter S (RTF-S) page 2 / 2

# for filter backwash in intervals

|  |  |
| --- | --- |
| **Backwash valve** |  |
| ball valve |  |  |
| housing + ball | stainless steel |
| packing | PTFE |
| with electrical drive |  |
|  |  |
| **Differential pressure gauging** |  |
| differential pressure manometer |  |
| static pressure | bar |  |
| measuring range | bar |  |
| with 2 adjustable micro-switches, with integrated inlet-pressure indicatorincl. cocks + screwings for connection to the differential pressure transmission pipe |
|  |  |
| **Electronic control unit** | for wall-attachment at site |
| housing | steel plate |
| protective system | IP 65 |
| dimensions: width x height x depth | 380 x 600 x 210 mm |
| working voltage | 230 V, 50 Hz |
| control voltage | 24 V DC |
| electrical cabling of all building components incl. polarized plug-type connectors  | Length 5 m  |
|  |  |
| **Filter cleaning effected by**  |  |
| differential pressure adjustable | 0 - 1,6 bar |
| time-flushing interval adjustable | continuously - 24 hours |
| flushing time adjustable | continuously - 24 hours |
|  |  |
| **Signal exchange with customer** |
| with potential free contact in the control cabinet | filter in operationfilter in flushing process (backwash valve opened / closed)collective fault |
| starting of flushing process  | from the control room |
| release of flushing process | from the control room |
|  |  |
| **Indicator lamp at the control cabinet** |
| after response of the collective fault indication the following faults will be indicated at the control cabinet: |
| either | faults in the filter operation |
| either | faults at the electrical drive |
| or | differential pressure too high |

|  |  |
| --- | --- |
| Manufacturer | Dango & Dienenthal Filtertechnik GmbH |
|  | +49 271 401 41 23 |